## Slide 1
Thyristor Switched Switch (TSC)
A Detailed Explanation of Structure and Principle
Power Electronics Technology Application Special Topic
Notes: Hello everyone, welcome to this technical sharing on Thyristor Switched Capacitor (TSC). Today, we will delve into the structure and core working principles of TSC, understanding how it becomes a key device for dynamic reactive power compensation in modern power systems. It is hoped that through this sharing, you will gain a comprehensive and in-depth understanding of this technology.

## Slide 2
CONTENTS
01 Definition and Core Value
Clearly define TSC and its core value positioning in the power system.
02 Core Working Principle
In-depth analysis of TSC's zero-crossing switching mechanism and operation logic.
03 Hardware Structure Analysis
Detailed analysis of the hardware composition of TSC controller and thyristor.
04 Key Features and Advantages
Compare with traditional contactors to demonstrate the technical advantages of TSC.
05 Typical Application Scenarios
Introduce practical application cases of TSC in industrial and power fields.
06 Selection Guide and Precautions
Provide practical equipment selection suggestions and on-site usage specifications.
Notes: This presentation will be divided into six parts. First, we will clarify the definition of TSC and its core value in power systems. Next, we will deeply analyze its core zero-crossing switching working principle. After that, we will detail the hardware structure of TSC. In the fourth part, we will show the key features and advantages of TSC compared to traditional contactors. The fifth part will introduce typical application scenarios of TSC in various fields. Finally, we will provide some practical selection guides and usage precautions.

## Slide 3
01 Definition and Core Value
Notes: First, let's enter Chapter 1 to understand what a Thyristor Switched Capacitor (TSC) is and why it plays an important role in power systems.

## Slide 4
What is a Thyristor Switched Switch (TSC)?
Core Definition: Solid-State Switch
A Thyristor Switched Switch (TSC) is a solid-state switch based on power electronics technology. It is used to switch capacitor banks on and off rapidly and without inrush current in low or medium voltage power grids to achieve dynamic reactive power compensation.
Core Advantage: Fast & No Surge
Compared to traditional mechanical switches, TSC uses thyristor devices to achieve zero-current switching, featuring fast response, no mechanical wear, and long lifespan, suitable for frequent switching applications.
System Position: Reactive Power Core
As the "heart" of the TSC system, it solves the bottleneck problems of traditional switches and is a key device for the stable operation of modern power systems.
Diagram: TSC Module in Reactive Power Compensation Device
Notes: Thyristor Switched Switch, referred to as TSC, is essentially a solid-state electronic switch. Its main function is to quickly connect or disconnect capacitor banks in the power grid, thereby achieving dynamic compensation of reactive power in the power grid.
Unlike traditional mechanical switches, TSC is based on power electronics technology, especially thyristor devices. Therefore, it has significant advantages such as fast speed, no inrush current, and long lifespan. It is the core component of a dynamic reactive power compensation system.

## Slide 5
Core Value of TSC: Solving the Pain Points of Traditional Contactors
Pain Points of Traditional Contactors
Huge Inrush Current: Inrush current reaches 20-50 times the rated value, impacting the power grid
Slow Response: Mechanical action takes hundreds of milliseconds, unable to compensate quickly
Limited Lifespan: Mechanical contacts are easily worn, with only tens of thousands of operations
Noise Pollution: Significant mechanical noise during switching operations
TSC Static Var Compensation Solution
Zero-Crossing Switching
Action at voltage/current zero crossing, inrush current suppressed within 2 times, no impact
Fast Dynamic Response
All-electronic switch responds in only 10-20ms, real-time tracking of load changes
Ultra-Long Maintenance-Free Lifespan
No mechanical moving parts, theoretical lifespan over one million times, extremely low maintenance cost
Quiet Operation
All-solid-state design, no noise during operation, improving the working environment
Notes: The core value of TSC lies in its perfect solution to the four major pain points of traditional AC contactors in reactive power compensation applications. First, contactors have huge inrush current when closing, while TSC reduces the inrush current to an extremely low level through zero-crossing switching technology. Secondly, contactors have slow response, while TSC's response time is in milliseconds, enabling real-time tracking of load changes. Third, contactors have short lifespan and are prone to damage due to mechanical contacts, while TSC has no moving parts, resulting in an extremely long lifespan and maintenance-free operation. Finally, TSC operates completely silently, solving the noise problem of contactors.

## Slide 6
02 Core Working Principle
Notes: Understanding the value of TSC, we naturally ask, how does it achieve these advantages? Next, we will delve into Chapter 2 to reveal the core working principle of TSC—zero-crossing switching technology.

## Slide 7
Core Principle: Zero-Crossing Switching Technology
Switching ON: Voltage Zero-Crossing
Precisely detect the grid voltage waveform and trigger the thyristor to conduct at the moment of the Voltage Zero-Crossing Point. Minimal inrush current.
Switching OFF: Current Zero-Crossing
Precisely detect the capacitor current waveform and stop triggering at the moment of the Current Zero-Crossing Point. Avoids overvoltage and arcing.
Notes: The core secret of TSC lies in its unique Zero-Crossing Switching Technology. In simple terms, it doesn't switch capacitors at arbitrary times but chooses two specific "zero" moments. When switching ON, it waits for the grid voltage to cross zero, ensuring minimal inrush current. When switching OFF, it waits for the capacitor current to cross zero, allowing thyristors to turn off naturally without arcing or overvoltage.

## Slide 8
Detailed ON Process
01 Detect Demand
The controller continuously monitors the reactive power or voltage of the power grid to determine the compensation demand.
02 Wait for Zero Point
Lock the best timing and wait for the grid voltage zero crossing.
03 Send Trigger Signal
At the moment of voltage zero crossing, send a trigger pulse to the anti-parallel thyristors.
04 Thyristor Conducts
The thyristors quickly respond and conduct, smoothly connecting the capacitor bank to the power grid.
05 Inrush-Free Switching ON
Voltage synchronization, inrush current is suppressed within twice the rated current.
Notes: Let's take a detailed look at the switching-on process. First, the controller detects that the power grid needs compensation. It doesn't act immediately but, like a patient sniper, waits for the best timing—the voltage zero crossing. At the moment the zero point arrives, it immediately issues a command to trigger the thyristors to conduct, connecting the capacitors to the power grid. Since the voltage of the capacitors and the power grid is synchronized at this time, there is almost no inrush current, achieving smooth switching-on.

## Slide 9
Detailed OFF Process
01 Detect Demand
The controller continuously monitors the grid status to determine if capacitor removal is needed to prevent over-compensation.
02 Wait for Zero Point
After detecting the demand, it starts waiting and precisely locks the zero-crossing moment of the capacitor current.
03 Stop Trigger Signal
At the precise moment of current zero crossing, the controller stops sending trigger pulses to the thyristor.
04 Thyristor Naturally Turns Off
The thyristor loses the trigger signal and the main current drops to zero, automatically turning off as a semi-controlled device.
05 Arc-Free Switching OFF
No arc is generated during the process, avoiding overvoltage and electromagnetic interference, achieving smooth and shock-free operation.
Notes: The OFF process is similar to the ON process, but the timing is chosen at the current zero crossing. When the system needs to remove a capacitor, the controller also waits for the current waveform to return to the zero point, then stops triggering the thyristor. Since the current is already zero at this time, the thyristor will turn off naturally. The entire process is quiet, arc-free, and has no impact on the power grid.

## Slide 10
03 Hardware Structure Analysis
Notes: Now that we understand the principle, let's take a look at the "body structure" of TSC. In Chapter 3, we will analyze the hardware structure of TSC in detail and see what key parts it consists of.

## Slide 11
TSC Main Circuit Structure
Anti-parallel Thyristor Module
Core component of each phase, realizing bidirectional conduction and turn-off control of AC current.
Capacitor Bank
Execution unit of reactive power compensation, providing required capacitive reactive power.
Series Reactor
Suppresses inrush current, limits harmonic current, and protects capacitors.
Protection & Auxiliary Circuit
Including RC snubber circuit (overvoltage protection) and fuse (short circuit protection) to ensure system reliability.
Three-phase System Wiring Method
Usually adopts Delta (△) or Star (Y) connection to meet different grid requirements.
Notes: This is the typical main circuit structure of TSC. The core is the anti-parallel thyristor module, which is connected in series with the capacitor and reactor. The reactor is very important as it can effectively suppress inrush current and filter harmonics. In addition, there are protection components such as RC snubber circuits and fuses. The entire three-phase circuit is usually connected in Delta or Star to adapt to different grid needs.

## Slide 12
Core Component: Anti-parallel Thyristor Module
Structure Principle: Bidirectional Current Control
The anti-parallel thyristor module is the core executive component that enables TSC to switch rapidly and without inrush current. It consists of two independent thyristors (SCRs) packaged in a single module in anti-parallel configuration, allowing bidirectional control of AC current.
Core Advantages: High Integration & Reliability
Modular design for easy installation. Excellent heat dissipation handles high current stress, directly determining the response speed and stability of the TSC device.
Notes: The heart of the TSC is this anti-parallel thyristor module. As you can see, it consists of two thyristors connected in anti-parallel. Why anti-parallel? Because alternating current has positive and negative half-cycles. One thyristor handles the positive half-cycle current, and the other handles the negative half-cycle, thus achieving complete control of the alternating current. The performance of this module directly determines the response speed and reliability of the entire TSC device.

## Slide 13
Control Unit and Protection Functions
Core Functions of Control Unit
Synchronous Sampling:Real-time collection of grid voltage and current signals to provide basis for calculation and judgment.
Zero-Crossing Detection:Accurate detection of voltage and current zero-crossing points, which is a prerequisite for zero-crossing switching.
Trigger Drive:Output trigger pulses to thyristor modules at precise moments according to control strategies.
Human-Machine Interaction:Provide parameter setting, status display, and fault alarm functions.
Comprehensive Protection Functions
Over-temperature Protection:Monitor the temperature of thyristor modules and automatically protect when overheated to prevent device damage.
Overcurrent/Short-Circuit Protection:Quickly cut off trigger signals when a fault is detected to protect equipment safety.
Phase Loss Protection:Prohibit switching and alarm when the grid is phase-lost to avoid abnormal operation.
Overvoltage/Undervoltage Protection:Take corresponding protection measures when the grid voltage is abnormal.
Notes: In addition to the main circuit, the control and protection system of TSC is also crucial. The control unit is like the "brain" of TSC, responsible for sampling, calculation, judgment, and issuing precise instructions. At the same time, to ensure the safe and reliable operation of the equipment, TSC is also equipped with comprehensive protection mechanisms, including over-temperature, overcurrent, phase loss, overvoltage, and other protection functions, just like putting on a strong "armor" for the equipment.

## Slide 14
04 Key Features and Advantages
Notes: Now that we understand the principles and structure of TSC, let's systematically summarize its key features and advantages compared to traditional solutions.

## Slide 15
TSC vs Traditional Contactor Performance Comparison
Performance Indicator
Thyristor Switched Switch (TSC)
Traditional AC Contactor
Switching Inrush Current
≤ 2x rated current, no impact
20-50x rated current, huge impact
Response Time
10-20ms, dynamic tracking for fast loads
Hundreds of ms, only for steady loads
Service Life
Over 1 million times, no mechanical wear
Tens of thousands of times, contact erosion
Operating Noise
No noise, fully solid-state operation
Significant mechanical noise
Maintenance Cost
Maintenance-free or very low cost
Regular inspection/replacement needed, high cost
Application Scenario
Arc furnaces, rolling mills, new energy, etc.
Pumps, fans, static compensation for steady loads
Notes: This table visually compares the performance of TSC and traditional contactors. From switching inrush current, response time, service life to operating noise and maintenance cost, TSC shows overwhelming advantages in all aspects. This also determines their completely different applicable scenarios: TSC is suitable for fast-fluctuating loads requiring high response speed and stability, while contactors are more suitable for relatively stable loads.

## Slide 16
05 Typical Application Scenarios
Notes: So, where exactly is TSC used? In Chapter 5, we will introduce some typical application scenarios of TSC.

## Slide 17
Wide Applications of TSC
Industrial Manufacturing
Used for dynamic reactive power compensation of impact loads such as arc furnaces and rolling mills, stabilizing voltage and improving power factor.
New Energy Power Generation
Suppresses reactive power and voltage fluctuations in wind and solar power plants to ensure stable grid operation.
Port Machinery
Provides rapid reactive power compensation for frequently starting and stopping equipment such as cranes and gantry cranes, reducing grid impact.
Power Quality Management
Works with LC filter switching branches to effectively suppress grid harmonic pollution and improve overall power quality.
Notes: With its excellent performance, TSC has a wide range of applications. In heavy industries such as steel and metallurgy, it can effectively handle impact loads from arc furnaces and rolling mills. In the new energy sector, both wind and solar power rely on TSC to suppress voltage fluctuations and ensure stable grid connection. At ports, TSC provides rapid reactive power support for frequently starting and stopping cranes. Additionally, it is widely used in power quality management to filter grid harmonics.

## Slide 18
06
Selection Guide and Precautions
Notes: Finally, in practical applications, how should we choose the appropriate TSC product? And what are the special considerations? Chapter 6 will provide you with some practical selection suggestions and precautions.

## Slide 19
Key Selection Parameters and Precautions
Core Technical Parameters Selection
Rated Voltage Matching
Must strictly match the grid system voltage (e.g., 400V, 690V) to ensure insulation safety.
Rated Capacity Calculation
Precisely calculate kvar value based on compensation requirements to ensure reactive power compensation effect.
Rated Current Margin
Module rated current must be greater than capacitor bank rated current to leave sufficient safety margin.
Harmonic Withstand Capability
In harmonic environments, select products with high harmonic withstand capability.
Control and Communication Interface
Choose manual/automatic control and communication protocols such as Modbus according to system requirements.
Installation and Usage Precautions
Must Series Reactor
Configure a reactor with 6%~7% reactance rate to suppress inrush current and filter harmonics, which is a prerequisite for safe operation.
Heat Dissipation and Ventilation
Thyristors generate heat during conduction; ensure sufficient heat dissipation space and ventilation, and install forced air cooling if necessary.
Control Power Supply Stability
Ensure stable power supply for the control unit, and that the voltage level matches the main circuit to prevent control failure.
Suitable Installation Environment
Should be installed in a dry, well-ventilated environment free of corrosive gases to avoid equipment aging.
Notes: When selecting a model, we mainly focus on several key parameters such as rated voltage, rated capacity, and rated current to ensure they match the on-site working conditions. At the same time, there are several precautions that must be kept in mind: First, TSC must be used in series with a reactor, which is a prerequisite for ensuring its safe operation; second, special attention should be paid to heat dissipation, because thyristors generate heat during operation; third, the stability of the control power supply is also very important. Following these principles can help us correctly and safely use TSC products.